## Application for connection of a
Form "Application for Connection of an Electricity Producer to TS SR"
Cases | 1) Connection of a new electricity source to TS
| 2) Change of installed capacity of the electricity source connected to TS |  |  |  |  | £
| 3) Reconnection of the electricity source to TS |  |  |  |  | £
| 4) Change of place and method of connection of the electricity source to TS |  |  |  |  | £
5) Expiry of validity of the Contract on Connection to TS
In case of a repeated application, provide name and date of the original application
Investment project name
1 | Identification data of an applicant (the applicant is a future owner of the facility(ies) or his authorized representative)
First name or name of the applicant from the Commercial Register
Address of the applicant registered office
| Contact person | Name and surname
Telephone
E-mail
Correspondence address
2 | Geographic name of the location where the facility(ies) is(are) connected
Region/City/Municipality
Cadastral area
Connection point to TS (TS node name / voltage level):
3 | Technical dimensioning of connection* of the Producer to TS [MVA] |  |  | Year of start/change (Y) | Year Y+5 | Year Y+10 | Year Y+15 | Year Y+20
- existing
- required increase
- total
4 | PARAMETERS OF SYNCHRONOUS GENERATORS (for each SG independently:
- Parameters of elements - according to sheet No. 2 to Form B3 (A. GENERATOR UNIT)
- Required increase of power in the relevant year [MW]
- Characteristics of the no-load SG (dependence of the stator voltage on the excitation current)
- No-load excitation current [A]
- P-Q diagram (with designated current limits of the turbine regulator - Pmax/Pmin and exciter regulator - Qmax/Qmin, determining the control area of the PQ diagram of the source, for the respective years)
| - Function and setting of the stator current limiter |  | / | / | / | / | / | /
5 | PARAMETERS OF EXCITERS (for every SG independently): |  |  | / | / | / | / | /
- Type of exciter
- Amplification / time constant of the exciter
- Structure and parameters of the voltage regulator
- Structure and parameters of the underexcitation limit regulator
- Function and setting of the rotor current limiter
6 | PARAMETERS OF PSS (type, structure, parametrization)
7 | PARAMETERS OFTURBINE REGULATORS:
- Structure and parameters of the power regulator and frequency corrector
- Block diagram
- Characteristics of valve opening P = f (opening)
8 | TURBINE PARAMETERS:
- Pmax – maximum power [MW]
- Pmin – minimum power [MW]
- Pmech – proportion of production of mech. power to the high-pressure, medium-pressure, low-pressure part
- R - statics of the frequency corrector
- VM – maximum speed of power increase
- Vm – maximum speed of power reduction
- TTURB – turbine time constant (high-pressure, medium-pressure, low-pressure part)
- DBf – insensitivity zone of the frequency corrector
9 | DATA ON PRODUCTION AND SELF-CONSUMPTION OF THE POWER PLANT IN THE PERIOD OF SUMMER MAXIMUM AND WINTER MAXIMUM (according to sheet No. 1 to Form B3)
10 | DATA ON TRANSFORMERS (according to sheet No. 2 to Form B3 - part B. TRANSFORMERS)
11 | DATA ON LINES (according to sheet No. 2 to Form B3 - part C. LINES)
12 | OVERVIEW DIAGRAM OF THE POWER PLANT TRANSMISSION AND RELEVANT PARAMETERS
Overview diagram of the power plant transmission shall include:
1 - Export of the electric power of the generator using block transformers and block line to ES SR.
2 - Main supply of self-consumption (VS) using tap-changing transformers VS
3 - Backup supply of VS using backup transformers VS - relation to the 110 kV system
4 - Connection of individual groups of asynchronous engines (AM), from the main VS switchyards up to:
4.1 - the main tap-changing VS transformer,
4.2 - backup VS transformer only if it is the backup VS transformer with direct connection to the 110 kV system
Parameters of elements contained in the overview diagram of the power plant transmission:
1 - Parameters of block transformers and block line of TS according to sheet No. 2 to Form B3, part B. TRANSFORMERS and C. LINE
2 - Parameters of tap-changing VS transformers according to sheet No. 2 to Form B3, part B. TRANSFORMERS
3 - Parameters of backup VS transformers (basic parameters Sn, Un, Ek)
4 - The data on asynchronous engines (AM) in self-consumption of power plants - while the summary of AM units in the amount exceeding 500 kW is sufficient, it is allocated to the respective AM group and related to the respective main VS switchyard (basic parameters of the AM groups are sufficient - number of engines, Pn group, Un, power factor, placement in the switchyard).
13 | OTHER INFORMATION
Other important information of the investor for the transmission system operator - assumed problems and narrow places in terms of power export of the power plant to ES or proposal of solutions of these narrow places in terms of own needs/interests (e.g. increase of reliability of power export, securing self-consumption etc.)
14
| Place: |  |  | Date:
| Filled in by: |  |  | Approved by:
|  | Name and surname |  |  | Name and surname of the statutory representative
|  | Signature |  |  | Seal and signature of the statutory representative
15 | Note:
* Technical dimensioning of the producer connection in the relevant connection point to TS is an amount of the installed apparent power of all generators of the electricity source expressed in MVA
Note on B33: Gelušiak Radovan: nezobrazuje sa posledné slovo

## 1. Production and self-consumpt
Table No.1 to Form of Application for Connection of a Producer to TS - Power Plant Production and Self-Consumption
Power Plant Production and Self-Consumption
Year |  | 1.) | PRODUCTION | [10 empty] | 2.) | SELF-CONSUMPTION |  | 3.) = 2.) -1.) | NET PRODUCTION (BALANCE) |  | NOTE
|  |  | Production unit | Type | Power | [9 empty] | - taken active/reactive power for self-consumption |  |  | ( + ) supply to the TS SR system
Turbine regulability - reserve P
[5 empty] | Instal. | Reached | Temp. decom. | Emerg: | Pg | Qg | Backup | PR | SR |  | Pvs | Qvs |  | ( Pg - Pvs ) | ( Qg - Qvs ) | For the PRODUCTION | for SELF-CONSUMPTION
[5 empty] | MW | MW | MW | MW | MW | MVAr | MW | ± [%] | ± [%] |  | MW | MVAr |  | MW | MVAr | Change | Change
Year of start or change (Y)
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+5) WM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+10) WM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+15) WM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+20) WM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
or if there are differences between WM and SM, to be provided for both periods
Year (Y+5) SM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+10) SM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+15) SM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Year (Y+20) SM
|  |  | Total | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0
Explanatory notes:
Year |  | - for the determined years Y, Y+5, Y+10, Y+15, Y+20 the data are provided: in the winter maximum (WM) for the period of years Y, Y+5, Y+10, Y+15, Y+20 (January) and in the summer maximum (SM) for the summer of the years Y, Y+5, Y+10, Y+15, Y+20 (July)
1.) PRODUCTION: |  | (Provide producer if there are currently production units available or if any sources are considered in the future)
Production unit |  | - name of individual production unit
Type |  | - thermal TE, captive ZE, hydroelectric VE, small hydroelectric MVE, steam-gas PPC, wind VtE
Instal. |  | - Installed power of the power plant - is a sum of the nominal active power of all generators of the power plant including the generators for house-load operation. Only the generators
which were decommissioned permanently from the power plant or which permanently lack the drive and serve as compensators
Reached |  | - The reachable power of the power plant - is the highest active power which may be achieved by the power plant in the monitored period in the respective state of the entire facility
and in case of normal operating conditions of the power plant
Temp. decom. |  | - Temporary decommissioning - due to general overhaul, common repair, reconstruction etc.
Emerg: |  | - The emergency power of the power plant - is the highest active power which may be achieved by the power plant within the certain period with regard to all technical and operating conditions
Pg, Qg |  | - estimated power supplied to the generator terminals used in the respective year
Backup |  | - difference (Emerg. - Supplied to terminals)
PR, SR |  | - regulation limits for primary/secondary regulation (technically achievable)
2.) SELF-CONSUMPTION:
Pvs / Qvs |  | - self-consumption active/reactive power
3.) NET PRODUCTION (BALANCE) : difference (Production - Self-consumption)
( Pg - Pvs ) |  | - net generation of active power
( Qvs - Qvs ) |  | - net generation of reactive power
NOTE:
for the PRODUCTION:
Change | - provide ROK (YEAR) plus N/R/Z/D (i.e. YEAR of change performance by new installation N / reconstruction R / cancellation Z / long-term outage D of the production block; in case of D it is necessary to mention the shutdown period)
for SELF-CONSUMPTION:
Change | - state the ROK (YEAR) in case of the demand change in self-consumption
Note on A4: Gelušiak Radovan: nezamknuté bunky (všetky)

## 2. Specifications of parameters
Table No. 2 to Form of Application for Connection of a Producer to TS - Specifications of Grid Elements Parameters
SPECIFICATIONS OF THE GRID ELEMENT PARAMETES
A. GENERATOR UNIT
Name | Sn | Un | cos jn | RSt | x´´dn | x´´ds | x2n | xdn | xds | xqn | xqs | x´dn | x´ds | x´qn | x´qs | x´´qn | x´´qs | xo | x1 | Ta | T´d | T´´d | T´q | T´´q | H | Tb | r = Ubmax/Ubn | Producer
| [MVA] | [kV] | [-] | [W] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [%] | [s] | [s] | [s] | [s] | [s] | [s] | [s] | [-]
Note:
| RSt | - resistance of a single phase of the stator winding
| x2n | - negative reactance in the unsaturated state
| xdn | - direct-axis synchronous reactance in the unsaturated state (%)
| xds | - direct-axis synchronous reactance in the saturated state (%)
| xqn | - quadrature-axis synchronous reactance in the unsaturated state (%)
| xqs | - quadrature-axis synchronous reactance in the saturated state (%)
| x´dn | - direct-axis transient reactance in the unsaturated state (%)
| x´ds | - direct-axis transient reactance in the saturated state (%)
| x´qn | - quadrature-axis transient reactance in the unsaturated state (%)
| x´qs | - quadrature-axis transient reactance in the saturated state (%)
| x´´dn | - direct-axis subtransient reactance in the unsaturated state (%)
| x´´ds | - direct-axis subtransient reactance in the saturated state (%)
| x´´qn | - quadrature-axis subtransient reactance in the unsaturated state (%)
| x´´qs | - quadrature-axis subtransient reactance in the saturated state (%)
| x0 | - zero-sequence reactance (%)
| x1 | - stray reactance of the rotor (%)
| Ta | - time constant of the direct-current component (s)
| T´d | - direct-axis transient time constant (s)
| T´´d | - direct-axis subtransient time constant (s)
| T´q | - quadrature-axis transient time constant (s)
| T´´q | - quadrature-axis sub transient time constant (s)
| H or Tj | - inertia constant (s)
| Tb | - time constant of the exciter (s)
| r = Ubmax/Ubn | - relative cap of the excitation voltage
B. TRANSFORMERS (BLOCK - for export of the source to TS SR, TAP-CHANGING - house transformer)
TRANSFORMER double winding
Name | Node_1 | Node_2 | Sn | ek | dPo | dPk | Io | Un1 | Un2 | Step | Angle | Tap+ | Tap- | Act_tap | Typ_reg | Aut_reg | Reg_pod_zaťaž | R0/R1 | X0/X1 | 1f. - 3f. | Mag. | Connection | Producer
| (prim. str.) | (sec. str.) | [MVA] | [%] | [kW] | [kW] | [%] | [kV] | [kV] | [%] | [deg] | [-] | [-] | [-] |  |  |  | [-] | [-] |  | circuit of | windings
TRANSFORMERS triplex winding
Name | Node_1 | Node_2 | Uzol_3 | Sn1 | Sn2 | Sn3 | ek12 | ek13 | ek23 | dPk12 | dPk13 | dPk23 | dPo | Io | Un1 | Un2 | Un3 | Step | Angle | Odb+ | Odb- | Akt_odb | Typ_reg | Aut_reg | Reg_under_ | R0/R1 | X0/X1 | 1f. - 3f. | Mag. | Connection | Producer
| (prim. str.) | (sec. str.) | (tert. str.) | [MVA] | [MVA] | [MVA] | [%] | [%] | [%] | [kW] | [kW] | [kW] | [kW] | [%] | [kV] | [kV] | [kV] | [%] | [deg] | [-] | [-] | [-] |  |  | load |  |  |  | circuit of | windings
Note:
| ek, dPk | - state to which power individual ek and dPk are related
| Step | - value of the additional voltage per one tap
| Angle | - angle of turning of additional voltage for regulation
| Tap+ | - maximum tap
| Tap- | - minimum tap
| Act_tap | - current tap
| Typ_reg | - type of regulation on the transformer: |  | [%]: s - on the secondary side
p - on the primary side
us - in the node on the secondary side
up - in the node on the primary side
| Aut_reg | - automatic voltage regulation: |  | [MVA]: 0 – is not
1 - on the primary side
2 - on the secondary side
| Reg_under_load | - regulation under load: |  | [MVA]: Y - yes
N - no
| 1.f - 3.f | 1-phase / 3-phase unit
| Mag. circuit: | J - core, P - sheath
C. LINE (EXTERNAL LINE, CABLE LINE) connecting the source to the TS SR
Name | Node_1 | Node_2 | R1 | X1 | B1 | Imax | limit_1 | limit_2 | R0 | X0 | B0 | Voltage | Length | Year of Construction | Owner | Overhead line
| (from where) | (to where) | [W] | [W] | [mS] | [A] | [A] | [A] | [W] | [W] | [mS] | [kV] | [km] |  |  | Kind of line | Line type | Tower type
Note:
R1 , X1 , B1 - consequent components
R0 , X0 , B0 - zero sequence components
Imax - with external lines provided data Idov in the summer
limit_1 (limit_2) - current limit of the feeder field in node_1 (node_2) for the respective ext. line, cable line [A]
Kind of the line - 1-system or 2-system
Type of the line - (e.g. AlFe240/39)
Type of the tower - (e.g. barrel, portal, etc.)